BR.W84Series

Eccentric rotary valve

INSTRUCTION

MANUAL

ZHEJIANG LASEN INTELLIGENT EQUIPMENT CO.,LTD

CATALOG

1. Acceptance, Handling and Storage	3

1. Acceptance and Handling	3

2. Storage	3

2. Product Overview and Features	5

3.Main technical parameters	6

3.1 Basic technical parameters	6

3.2 Flow Characteristics	6

3.3 Material	7

3.4 Allowable differential pressure	8

3.5 Accessories	9

4. Installation	13

4.1. Installation Notes	13

4.2. Allowable ambient temperature of installation site	13

4.3. Maintenance Space	13

4.4. Installation Locations	14

4.5. Piping and wiring	14

4.6 Preparation before operation	14

5. Maintenance	16

5.1. Analysis	16

5.2. Maintenance and replacement steps	16

6. Troubleshooting	17

7. Common accessories and functions	19

8. Instructions for ordering	19

# 1. Acceptance, Handling and Storage

## 1. Acceptance and Handling

- When the valve is unpacked, the received equipment shall be inspected according to

- the packing list. Eng objects. Check Appendix III for the weight of this valve.  The packing box (wooden box) contains the product instruction, packing list, certificate of conformity and otach packing box is equipped with a list of valves and their

- accessories.  Use hoisting machinery for loading, unloading and handling to prevent damage to

- the connecting pipes and installed valve accessories. Do not stand or operate hoisting

- machinery under hoistiher documents.  In the process of handling, pay attention not to make the valve collide violently, otherwise it will cause some performance degradation and need to be re debugged. It

- may even make the control valve act badly, and affect the regulating quality.

## 2. Storage

- Before the valve is mounted on the pipeline, it must be kept in packing state.

- Do not keep the valve in the following places：

·Places where the valve may caught in the rain.

·High temperature(over 60 ℃) places.

·Dusty places.

·Places with high humidity.

·Places with corrosive medium.

- If the package is unpacked due to performance inspection during acceptance, it must be repacked and kept in packing stage until mounting.

- Please do not open the plugs and covers of air piping and electrical wiring before air piping work and electrical wiring work.

- If the storage period is more than one year, the packing often hardens and ages, so please open the packing, loosen the hexagon nut fastening the packing for 2 turns, keep it in this state, and then tighten it when using, and compress the packing. Then apply the air pressure (nitrogen in case of more than 0.95mpa) or water pressure equivalent to the use of fluid pressure from the piping flange, and check whether there is any leakage in the packing part. If there is any leakage, please replace the new packing. When replacing the packing, pay attention not to damage the surface of valve stem. When filling the packing, press the packing into the stuffing box vertically and horizontally.

- For storage after use, please handle as follows:

- Please clean the inside of the control valve with water carefully and dry it.

- Please do not damage the sealing surface of the connecting flange between the valve body and the piping.

- Please conduct antirust treatment for the parts that may rust.

- Please waterproof the air piping interface and electrical piping interface.

# 2. Product Overview and Features

The BR.W84 series pneumatic eccentric rotary control valve (also known as cam deflection valve) adopts Masoneilan technology combined with the characteristics of China, and combines the advantages of single seat valves, ball valves, butterfly valves, etc. It has outstanding advantages such as simple structure, small volume, light weight, large rated flow coefficient, large adjustable range, wide temperature range, small leakage, and good stability. Due to the fact that the plug and stem only rotate, the friction force they experience during operation is very small. When the plug and seat are in contact and closed, the plug deflection arm generates small elastic deformation and elastic tightening force under the thrust of the executing structure, making the contact between the plug and valve seat more tight and firm. Therefore, the leakage of the eccentric valve is very small. The actuator thrust required to close the valve is smaller than that of ball valves and butterfly valves. Therefore, this series of products is widely used in automatic control systems for industrial processes such as chemical, metallurgical, and power plants.

# 3.Main technical parameters

## 3.1 Basic technical parameters

| Size | 1＂ | ＂ | 2＂ | 3＂ | 4＂ | 6＂ | 8＂ | 10＂ | 12＂ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flow Coefficient Cv | 14 | 30 | 50 | 135 | 230 | 500 | 850 | 1300 | 1750 |
|  | 8.4 | 18 | 30 | 81 | 138 | 300 | 510 | 780 | 1050 |
|  | 5.6 | 12 | 20 | 54 | 92 | 200 | 340 | 520 | 700 |
| Characteristics | Approximate value line (logarithmic linearity and other characteristics must be equipped with positioners) |
| PN | ANSI 150 300 600 |
| Travel | 50° |
| Leakage | ANSI B16 104 Ⅳ（Metal seal） Ⅵ（Soft seal） |
| Operating temperature ℃ | -195～+400 |
| rangeability | 100∶1 |
| Actuator | Diaphram | DL1 | DL2 | DL3 |
|  | Piston | PL1 | PL2 | PL3 | PL4 |
| Connection | Flange |

## 3.2 Flow Characteristics

## 3.3 Material

| No. | Part name | Material |
| --- | --- | --- |
| 1 | Body | WCB SCS13 SCS14 ZG25 ZGlCr18Ni9 ZG0Cr18Ni12Mo2Ti |
| 2 | Guide sleeve | 9Cr18 SUS316+ST |
| 3 | Seat | 0Cr18Ni12Mo2Ti SUS316+ST |
| 4 | Plug | SUS316+ST |
| 5 | Ring nut | 0Cr18Ni12Mo2Ti SUS316+ST |
| 6 | Guide sleeve | 9Cr18 SUS316+ST |
| 7 | Stem | 0Cr18Ni12Mo2Ti SUS316 |
| 8 | Gasket | 1Cr18Ni9 0Cr18Ni12Mo2Ti |
| 9 | Packing | PTFE+asbestos or graphite |
| 10 | Packing bolt | 1Cr18Ni9 |
| 11 | Packing gland | 1Cr18Ni9 |
| 12 | Plate | ZG25 ZG1Cr18Ni9 |
| 13 | Nut | 1Cr18Ni9 |

## 3.4 Allowable differential pressure

（1）Metal seal  Unit：MPa

| DN | Cv | Air flow open type | Air on flow off type or air off flow on type |
| --- | --- | --- | --- |
|  |  |  | Air supply pressure |
|  |  |  | 0.14 | 0.18 | 0.21 | 0.25 | 0.28 | 0.32 | 0.35 | 0.39 | 0.42 | 0.46 | 0.49 | 0.53 |
| 1＂ | 14 5.6 | 7.0 10.2 | 7.0 10.0 |  |  |  |  |  |  |  |  |  |  |  |
| ＂ | 30 12 | 4.7 9.8 | 3.0 6.3 | 5.6 10.2 |  |  |  |  |  |  |  |  |  |  |
| 2＂ | 50 20 | 2.5 5.2 | 1.6 3.3 | 3.5 7.0 | 4.2 7.0 |  |  |  |  |  |  |  |  |  |
| 3＂ | 135 54 | 2.0 4.5 | 1.3 2.8 | 2.7 6.1 | 4.2 7.0 |  |  |  |  |  |  |  |  |  |
| 4＂ | 230 92 | 1.0 2.2 | 0.63 1.4 | 1.4 3.0 | 2.2 4.9 | 3.1 6.8 | 3.9 7.0 | 4.1 7.0 |  |  |  |  |  |  |
| 6＂ | 500 | 0.63 |  |  | 0.35 0.35 0.35 | 0.91 0.91 0.91 | 1.4 1.4 1.4 | 2.1 2.1 2.1 | 2.5 2.5 | 3.1 3.1 | 3.7 3.7 | 4.2 4.2 |  |  |
|  | 200 | 1.4 |  |  | 0.77 0.77 0.77 | 2.0 2.0 2.0 | 3.2 3.2 3.2 | 4.4 4.4 3.5 | 5.6 5.6 | 6.8 6.8 | 7.0 7.0 |  |  |  |
| 8＂ | 850 | 0.32 |  |  | 0.18 0.18 0.18 | 0.42 0.42 0.42 | 0.7 0.7 0.63 | 1.0 1.0 | 1.3 1.3 | 1.5 | 1.8 | 2.1 | 2.4 | 2.5 |
|  | 510 | 0.49 |  |  | 0.28 0.28 0.28 | 0.7 0.7 0.7 | 1.1 1.1 1.0 | 1.5 1.5 | 2.0 2.0 | 2.4 | 2.8 | 3.2 | 3.7 | 3.9 |
|  | 340 | 0.77 |  |  | 0.42 0.42 0.42 | 1.1 1.1 1.0 | 1.8 1.8 1.5 | 2.5 2.5 | 3.2 3.2 | 3.9 | 4.5 | 5.2 | 5.9 | 6.3 |
| 10＂ | 1300 | 0.18 |  |  | 0.11 0.11 0.11 | 0.25 0.25 0.25 | 0.38 0.35 0.38 | 0.56 0.56 | 0.7 0.7 | 0.84 | 0.98 | 1.1 | 1.3 | 1.5 |
|  | 780 | 0.42 |  |  | 0.14 0.14 0.14 | 0.35 0.35 0.35 | 0.56 0.56 0.49 | 0.84 0.84 | 1.1 1.1 | 1.3 | 1.5 | 1.8 | 2.0 | 2.2 |
|  | 520 | 0.42 |  |  | 0.25 0.25 0.25 | 0.63 0.63 0.63 | 0.98 0.98 0.84 | 1.3 1.3 | 1.7 1.7 | 2.1 | 2.5 | 2.8 | 3.2 | 3.6 |
| 12＂ | 1750 | 0.11 |  |  |  | 0.14 0.14 0.14 | 0.21 0.21 0.621 | 0.32 0.32 | 0.39 0.39 | 0.49 0.42 | 0.56 | 0.63 | 0.7 | 0.84 |
|  | 1050 | 0.14 |  |  | 0.07 0.07 0.07 | 0.21 0.21 0.21 | 0.35 0.35 0.32 | 0.49 0.49 | 0.63 0.63 | 0.7 | 0.84 | 0.98 | 1.1 | 1.3 |
|  | 700 | 0.25 |  |  | 0.14 0.14 0.14 | 0.35 0.35 0.35 | 0.56 0.56 0.49 | 0.77 0.77 | 0.98 0.98 | 1.3 | 1.5 | 1.7 | 1.9 | 2.1 |

（2）Soft seal  Unit：MPa

| DN | Cv | Air flow open type | Air on flow off type or air off flow on type |
| --- | --- | --- | --- |
|  |  |  | Air supply pressure |
|  |  |  | 0.14 | 0.18 | 0.21 | 0.25 | 0.28 | 0.32 | 0.35 | 0.39 | 0.42 | 0.46 | 0.49 | 0.53 |
| 1＂ | 14 5.6 | 5.6 7.0 | 5.6 7.0 |  |  |  |  |  |  |  |  |  |  |  |
| ＂ | 30 12 | 3.5 7.0 | 1.6 3.7 | 4.9 7.0 |  |  |  |  |  |  |  |  |  |  |
| 2＂ | 50 20 | 1.8 3.7 | 0.7 1.6 | 2.6 5.3 | 4.2 7.0 |  |  |  |  |  |  |  |  |  |
| 3＂ | 135 54 | 1.4 3.4 | 0.62 1.6 | 2.1 4.8 | 3.5 5.6 |  |  |  |  |  |  |  |  |  |
| 4＂ | 230 92 | 0.7 1.6 | 0.25 0.7 | 1.1 2.3 | 1.8 4.0 | 2.6 5.6 | 3.4 5.6 | 3.5 5.6 |  |  |  |  |  |  |
| 6＂ | 500 | 0.42 |  |  | 0.14 0.14 0.14 | 0.63 0.63 0.63 | 1.2 1.2 1.2 | 1.7 1.7 1.7 | 2.2 2.2 2.5 | 2.7 2.7 | 3.2 3.2 | 3.5 3.5 |  |  |
|  | 200 | 1.1 |  |  | 0.42 0.42 0.42 | 1.5 1.5 1.5 | 2.7 2.7 2.7 | 3.7 3.7 3.7 | 4.8 4.8 | 5.6 5.6 |  |  |  |  |
| 8＂ | 850 | 0.14 |  |  |  | 0.28 0.28 0.28 | 0.52 0.52 0.52 | 0.77 0.77 0.63 | 1.1 1.1 | 1.3 1.3 | 1.5 | 1.8 | 2.1 |  |
|  | 510 | 0.28 |  |  | 0.07 0.07 0.07 | 0.46 0.46 0.46 | 0.84 0.84 0.84 | 1.2 1.2 0.96 | 1.6 1.6 | 2.0 2.0 | 2.4 | 2.8 | 3.2 |  |
|  | 340 | 0.49 |  |  | 0.14 0.14 0.14 | 0.77 0.77 0.77 | 1.4 1.4 1.4 | 2.0 2.0 1.5 | 2.6 2.6 | 3.2 3.2 | 3.8 | 4.4 | 4.9 |  |
| 10＂ | 1300 |  |  |  |  | 0.11 0.11 0.11 | 0.25 0.25 0.25 | 0.38 0.38 0.35 | 0.53 0.53 | 0.67 0.67 | 0.77 0.70 | 0.91 | 1.1 | 1.2 |
|  | 780 | 1.1 |  |  |  | 0.21 0.21 0.21 | 0.42 0.42 0.42 | 0.63 0.63 0.63 | 0.84 0.84 | 1.1 1.1 | 1.3 | 1.5 | 1.7 | 1.9 |
|  | 520 | 0.21 |  |  |  | 0.35 0.35 0.35 | 0.7 0.7 0.7 | 1.1 1.1 0.84 | 1.3 1.3 | 1.7 1.7 | 2.0 | 2.3 | 2.7 | 3.0 |
| 12＂ | 1750 |  |  |  |  | 0.04 0.04 0.04 | 0.11 0.11 0.11 | 0.18 0.18 0.18 | 0.28 0.28 0.21 | 0.35 0.35 | 0.42 0.42 | 0.49 | 0.6 | 0.67 |
|  | 1050 |  |  |  |  | 0.07 0.07 0.07 | 0.21 0.21 0.21 | 0.32 0.32 0.32 | 0.46 0.46 | 0.56 0.56 | 0.7 | 0.77 | 0.91 | 1.1 |
|  | 700 | 0.07 |  |  |  | 0.18 0.18 0.18 | 0.35 0.35 0.35 | 0.56 0.56 0.56 | 0.77 0.77 | 0.91 0.91 | 1.1 0.90 | 1.3 | 1.5 | 1.8 |

Note: 1. If the allowable differential pressure exceeds the table value, it is recommended to use a piston type actuator.

2. If the Cv value is greater than 500, it is recommended to use a piston type actuator.

3. The allowable differential pressure does not exceed the nominal pressure of the valve.

## 3.5 Accessories

Due to the approximate linear flow characteristics of the BR.W84 series pneumatic eccentric rotary control valve, positioners, including filter regulators, are generally required in situations with control accuracy requirements. In addition, according to process requirements, auxiliary components such as electrical converters, lock valves, safety valves, limited switches, solenoid valves, etc. can also be equipped.

The handwheel of the BR.W84 series is integrated with the valve, and users can supply it without specifying it when ordering.

Overall dimensions and weight

- Equipped with rolling diaphragm actuator  Unit：mm

ANSI 150#

| DN | A | B | C | D | E | F | G | J | K | L | ΦM | ΦN | n-Φ | Weight（Kg） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1＂ | 102 | 173 | 297 | 208 | 163 | 140 | 110 | 206 | 38 | 137 | 110 | 79.5 | 4 - 16 | 15 |
| ＂ | 161 | 175 | 300 | 211 | 163 | 140 | 110 | 234 | 51 | 165 | 130 | 98.5 | 4 - 16 | 18 |
| 2＂ | 162 | 175 | 300 | 211 | 163 | 140 | 110 | 239 | 66 | 170 | 150 | 120.5 | 4 - 18 | 21 |
| 3＂ | 196 | 262 | 434 | 229 | 163 | 175 | 118 | 333 | 84 | 244 | 190 | 152.5 | 4 - 18 | 48 |
| 4＂ | 236 | 264 | 437 | 229 | 163 | 175 | 118 | 356 | 109 | 267 | 230 | 190.5 | 8 - 18 | 54 |
| 6＂ | 230 | 330 | 533 | 302 | 254 | 218 | 197 | 432 | 147 | 323 | 280 | 241.5 | 8 - 22 | 100 |
| 8＂ | 280 | 333 | 536 | 305 | 254 | 218 | 197 | 470 | 203 | 361 | 345 | 298.5 | 8 - 22 | 150 |
| 10＂ | 334 | 335 | 538 | 310 | 254 | 218 | 197 | 547 | 251 | 465 | 405 | 362 | 12 - 26 | 188 |
| 12＂ | 338 | 338 | 541 | 312 | 254 | 218 | 197 | 610 | 277 | 500 | 485 | 432 | 12 - 26 | 234 |

ANSI 300#

| DN | A | B | C | D | E | F | G | J | K | L | ΦM | ΦN | n-Φ | Weight（Kg） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1＂ | 102 | 173 | 297 | 208 | 163 | 140 | 110 | 206 | 38 | 137 | 125 | 89 | 4 - 18 | 15 |
| ＂ | 161 | 175 | 300 | 211 | 163 | 140 | 110 | 234 | 51 | 165 | 155 | 114.5 | 4 - 22 | 19 |
| 2＂ | 162 | 175 | 300 | 211 | 163 | 140 | 110 | 239 | 66 | 170 | 165 | 127 | 8 - 18 | 22 |
| 3＂ | 196 | 262 | 434 | 229 | 163 | 175 | 118 | 333 | 84 | 244 | 210 | 168.5 | 8 - 22 | 47 |
| 4＂ | 236 | 264 | 437 | 229 | 163 | 175 | 118 | 356 | 109 | 267 | 255 | 200 | 8 - 22 | 68 |
| 6＂ | 230 | 330 | 533 | 302 | 254 | 218 | 197 | 432 | 147 | 323 | 320 | 270 | 12 - 22 | 118 |
| 8＂ | 280 | 333 | 536 | 305 | 254 | 218 | 197 | 470 | 203 | 361 | 380 | 330 | 12 – 26 | 177 |
| 10＂ | 334 | 335 | 538 | 310 | 254 | 218 | 197 | 547 | 251 | 465 | 445 | 387.5 | 16 – 30 | 226 |
| 12＂ | 338 | 338 | 541 | 312 | 254 | 218 | 197 | 610 | 277 | 500 | 520 | 451 | 16 – 33 | 284 |

ANSI 600#

| DN | A | B | C | D | E | F | G | J | K | L | ΦM | ΦN | n-Φ | Weight（Kg） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1＂ | 102 | 173 | 297 | 208 | 163 | 140 | 110 | 206 | 38 | 137 | 125 | 89 | 4 – 18 | 15 |
| ＂ | 161 | 175 | 300 | 211 | 163 | 140 | 110 | 234 | 51 | 165 | 155 | 114.5 | 4 – 22 | 20 |
| 2＂ | 162 | 175 | 300 | 211 | 163 | 140 | 110 | 239 | 66 | 170 | 165 | 127 | 8 – 18 | 24 |
| 3＂ | 196 | 262 | 434 | 229 | 163 | 175 | 118 | 333 | 84 | 244 | 210 | 168.5 | 8 – 22 | 49 |
| 4＂ | 236 | 264 | 437 | 229 | 163 | 175 | 118 | 356 | 109 | 267 | 275 | 216 | 8 – 26 | 78 |
| 6＂ | 230 | 330 | 533 | 302 | 254 | 218 | 197 | 432 | 147 | 323 | 355 | 292 | 12 – 30 | 146 |
| 8＂ | 280 | 333 | 536 | 305 | 254 | 218 | 197 | 470 | 203 | 361 | 420 | 349 | 12 – 33 | 217 |
| 10＂ | 334 | 335 | 538 | 310 | 254 | 218 | 197 | 547 | 251 | 465 | 510 | 432 | 16 – 36 | 296 |
| 12＂ | 338 | 338 | 541 | 312 | 254 | 218 | 197 | 610 | 277 | 500 | 560 | 489 | 20 - 36 | 354 |

List of connecting bolts and nuts between valve and pipeline

| HG | 150# | 300# | 600# |
| --- | --- | --- | --- |
| DN SPE | M×L | b | Bolts QTY | Nuts QTY | M×L | b | Bolts QTY | Nuts QTY | M×L | b | Bolts QTY | Nuts QTY |
| 25 | M14×185 | 30 | 4 | 8 | M16×195 | 35 | 4 | 8 | M18×210 | 40 | 4 | 8 |
| 40 | M14×200 | 30 | 4 | 8 | M20×225 | 40 | 4 | 8 | M20×235 | 40 | 4 | 8 |
| 50 | M16×225 | 35 | 4 | 8 | M16×230 M16×95* | 40 | 7 2 | 14 2 | M18×250 M18×105* | 40 | 7 2 | 14 2 |
| 80 | M18×270 | 35 | 4 | 8 | M20×305 M20×130* | 40 | 7 2 | 14 2 | M20×310 M20×140* | 40 | 7 2 | 14 2 |
| 100 | M18×295 M18×105* | 40 | 7 2 | 14 2 | M20×320 M20×135* | 40 | 7 2 | 14 2 | M22×355 M22×150* | 45 | 7 2 | 14 2 |
| 150 | M20×355 M20×120* | 40 | 7 2 | 14 2 | M20×365 M20×150* | 45 | 11 2 | 22 2 | M27×420 M27×170* | 50 | 11 2 | 22 2 |
| 200 | M20×365 M20×105* | 40 | 6 4 | 12 4 | M24×405 M24×125* | 50 45 | 10 4 | 20 4 | M30×460 M30×150* | 55 45 | 10 4 | 20 4 |
| 250 | M22×425 M22×110* | 40 | 8 8 | 16 8 | M27×475 M27×130* | 50 45 | 12 8 | 24 8 | M33×535 M33×165* | 65 45 | 12 8 | 24 8 |
| 300 | M22×470 M22×110* | 45 | 8 8 | 16 8 | M30×525 M30×140* | 65 45 | 12 8 | 24 8 | M33×580 M33×165* | 65 50 | 16 8 | 32 8 |

Note: "*" indicates short double head studs

# 4. Installation

## 4.1. Installation Notes

In order to maintain the performance of this control valve, please pay attention to the following during installation:

- Do not damage the sealing surface of the connecting flange between the valve and the piping, so as to avoid sealing leakage.

- When the valve is taken out of the packing box, it is recommended to use sling to lift if the valve is heavy. The lifting weight of sling must be consistent with the weight of the valve to avoid damage to the valve.

- Please fully clean the inside of the piping, remove the sundries and welding slag before install the valve. If there is any foreign matter, it will cause leakage between the valve core and the valve seat.

- Please do not open the plug and cover of the air piping and electrical wiring interface after the installation of the valve and piping and before the air piping and electrical wiring works are started.

- When the valve is installed on the process piping, please do not make it subject to impact, fall and other severe impact. Otherwise, it will cause failure and must be re debugged.

- When the valve actuator is equipped with manual operation mechanism, a safe and easy operation site shall be ensured.

- When there is vibration on the installation pipeline or the valve diameter is large (the valve weight is heavy), the support frame shall be installed. Do not install the valve in the situation of severe vibration and excessive load on the valve.

- To facilitate maintenance, do not install the actuator upside down.

- Before installation, the pipeline shall be cleaned. Sufficient length of straight pipe shall be reserved at the valve inlet, and the filter shall be equipped at the front of the valve inlet as far as possible. Pay attention to the coaxiality when the pipeline flange is connected with the valve body flange.

## 4.2. Allowable ambient temperature of installation site

The ambient temperature for the installation and use of the valve must be in accordance with the ambient temperature provided in the technical data sheet when ordering the valve. Exceeding the specified ambient temperature may cause unexpected failure or even accident.

If there is no special instruction, the valve is generally used in the environment temperature: - 25 ℃ ~ 70 ℃.

## 4.3. Maintenance Space

The space for replacing the actuator and checking the valve internals shall be reserved above the valve.

- For the convenience of maintenance, a bypass valve with the same flow characteristics and stroke as the valve can be set. As shown in Fig. 3-1, the dotted line indicates another allowable direction of pipeline access.

## 4.4. Installation Locations

- When installing on the dangerous pipeline with vibration and external force, please use the valve attached bracket or piping bracket.

- For the occasion with handwheel, please make sure it is a safe and easy to operate installation position.

- When the medium flows through the valve, its flow direction shall be consistent with the arrow direction on the valve body.

## 4.5. Piping and wiring

- The solenoid valve, limit switch, etc. installed according to the user's requirements are delivered after assembly with the actuator, please take care not to damage them.

- When the valve is equipped with accessories, the instrument of piping and wiring shall be carried out according to the installation instructions of each accessory.

- Please use the sealing tape carefully at the connection part of the accessory piping, or do not use the sealing tape, so as to avoid blocking the gas path and causing the poor action of the accessory.

- In order to guarantee the performance of accessories, please select appropriate wire specifications.

- In the wiring process, the external wire interface shall be sealed and waterproof, and the wiring shall be strictly checked in explosion-proof occasions to ensure that the interface part meets the explosion-proof requirements, so as to avoid electric leakage and fire.

## 4.6 Preparation before operation

After valve installation, please do the following before commissioning

  - Before connecting the accessories that need to be connected to the power supply, please confirm whether the power supply voltage is consistent with the power supply voltage indicated on the accessory nameplate.

  - The operating air source of the actuator shall be dry and clean air, and the air source pressure shall not exceed the marked range. If there is any change, please contact our company.

  - Make sure that there is no air leakage at the connection of instrument air piping and the fastening part of diaphragm (outside the actuator). In case of leakage, please refer to the maintenance part of the actuator in this manual for maintenance and plugging, or contact our company.

  - Accessory debugging: if debugging is needed, please refer to the operation manual of each accessory. When debugging the positioner to detect the valve stroke, please use a dial indicator or a stroke detection instrument equivalent to the dial indicator.

For pneumatic valves with handwheel accessories, please manually operate the valve switch after cutting off the air supply. For manual operation, please pull out the flat handle first, turn to the manual position, and then turn the hand wheel. When the hand wheel rotates clockwise, the valve will close, otherwise, the valve will open.

# 5. Maintenance

## 5.1. Analysis

The valve is mainly used for wear of components, especially the valve seat, valve plug and packing. In application, the valve needs to be checked regularly to prevent possible failure.

- If leakage occurs, it may be caused by packing damage or metal bellows seal failure.

- If the valve cannot be shut off, it may be caused by the stuck magazine between seat and plug, or the sealing surface of the valve seat and the valve plug is damaged. Thoroughly clean or remove the defective valve trim and replace it.

## 5.2. Maintenance and replacement steps

1. Loosen the hexagonal nut on the packing press plate, remove the packing press plate and packing sleeve;

2. Loosen the hexagonal nut on the valve body stud and remove the bonnet from the valve body. At this time, the stem and plug will be pulled out together, and the pulling process should be vertical to avoid scratching the guide sleeve, stem, and plug;

3. Pull out the stem from the opposite direction of the packing, and do not scratch the guide sleeve and plug during this process;

4. Remove the packing and other components from the packing section of the bonnet;

5. Do not disassemble the seat without any abnormalities on the sealing surface.

After the disassembly is completed, please wipe all parts clean with a cloth. If the wiping is not clean, clean them with solvent, then rinse them with water, and let them dry thoroughly. Then carefully inspect all parts for damage. If there are any, please replace them with new ones. After each inspection, the sealing surface between the seat and the plug must be ground.

When tightening the bolts and nuts connecting the plug and bracket, the bonnet and packing pressure plate, and the bonnet and valve body, it is necessary to work evenly.

Pay attention to protecting the mating step surface between the bonnet and valve body, as well as the mating surface between the stem and guide sleeve.

When installing the seat and plug, please be careful not to damage the sealing surface between the plug and seat.

Be careful not to damage the stem when installing the packing.

If any abnormal situations are found during the inspection and cannot be handled, please contact us.

# 6. Troubleshooting

- Regular inspection and maintenance shall be carried out according to the site operation.

- If any abnormality is found during regular inspection or failure occurs during operation, please refer to the following table for maintenance. If you can't solve the problem, please contact us.

| Common abnormality | Causes | Corresponding Troubleshooting |
| --- | --- | --- |
| There is an input signal but no action or slow action | Air supply pressure below requirement | Supply specified air pressure |
|  | Blocked or leaking air piping | Clean, reinforce or replace the air piping |
|  | Air leakage in the fastening part of the diaphragm | Reinforcement, dismantling, renovation or replacement |
|  | Air leakage in the push rod section | Remove and replace the O-ring |
|  | Abnormal accessories such as positioner and solenoid valves | Without connecting the accessories, apply the specified air pressure to the actuator. If there are no abnormalities, adjust the positioner or repair or replace the accessories |
|  | Abnormal valve body or actuator parts | Remove the bracket and refer to Section 5 for maintenance of the actuator and valve body. |
|  | Insufficient sensitivity of the positioner | Please refer to the positioner manual |
| Excessive valve leakage | Damaged sealing gasket | Replace it |
|  | Damaged sealing surface between seat and plug | Grinding or replacement |
|  | Insufficient thrust of the actuator | Replace the actuator |
| The valve action is unstable and there is vibration | Insufficient thrust of the actuator | Replace the actuator |
|  | The output signal of the positioner changes | Adjust various settings of the positioner and check the signal system |
|  | Excessive fluctuation in gas supply pressure | Determine and replace the diameter of the gas supply piping |
|  | Filter regulator faulty | Repair and replace the filter regulator |
| Leakage of sealing packing | The packing gland is not tightly pressed | Press the gland tightly |
|  | Damaged packing | Replace the packing |
|  | Damaged stem | Replace the stem |
| Leakage at the connection between the valve body and the bonnet | Damaged sealing gasket | Replace the sealing gasket |
|  | Loose hexagonal nut | Tighten the hex nut |

# 7. Common accessories and functions

- Positioner: By improving the regulating precision of the valve, the valve can be controlled in different ranges.

- Electric and pneumatic converter: converts the change of electric signal from sensors or other control instruments into the air pressure signal that causes the actuator to make corresponding action, and inputs it to the actuator to make the actuator act.

- Filter Regulator: Input the air source into the positioner or actuator after air purification,  pressure decompression and stabilization

- Handwheel: In case of any abnormality in the current control system, such as loss of gas or power, the control requirements can be achieved by manual operation. The handwheel mechanism is installed on the actuator and connected with the upper diaphragm cover of the actuator.

# 8. Instructions for ordering

- Product model and name

- Nominal pressure

- Nominal diameter

- Pressure before and after the valve

- Medium, density and temperature

- Medium’s maximum, normal and minimum flow

- Inherent flow characteristics of valve

- Overall action mode, gas source pressure, signal range

- Valve body and trim material

- Explosion proof requirements

- Accessories and other special requirements

ZHEJIANG LASEN INTELLIGENT EQUIPMENT CO.,LTD ADD:No. 15 Mashan Road, Changkou Industrial Zone, Fuyang District, Hangzhou, Zhejiang Province TEL:0571-23252111/23291601 FAX:0571-23291602 WEB:www.lasen.com.cn POST CODE:311401

# Text boxes

图2-1

D

C

A

B

Fig. 3-1

D

C

B

A